## BOQ
S No | Item Code | Description of Item | Unit | Qty | Unit Price | Freight Charges
1 | SUE400001 | 40/50MVA, 220/33kV, ONAN/ ONAF new transformer along with OLTC, remote tap changer panel, for this transformer and all accessories | Nos | 2
1.1 | SUEON0001 | On line DGA monitoring for each transformer working on spectroscopy method. | Nos | 2
1.2 | SUENI0001 | Nitrogen Injection Fire Protection System (NIFPS) for 40/50MVA Transformers | Nos | 2
2 | SUE220004 | 220 kV Lighting Arrestor | Nos
2.1 | SUE190001 | 198 kV, Class III, 10 kA, lightning arrestor along with Surge monitor | Nos | 12
3 | SUE220005 | 220 kV Isolator/ Disconnecting Switches | Nos | 0
3.1 | SUECE0001 | Centre break tandom isolator (Double Break) 245kV, 2000A, 40kA for 3Sec. | Nos | 5
3.2 | SUECE0002 | Centre break isolator with one Earth switch (Double Break) 245kV, 2000A, 40kA for 3Sec. | Nos | 8
3.3 | SUECE0003 | Centre break tandom isolator with one Earth switch (Double Break) 245kV, 2000A, 40kA for 3Sec. | Nos | 1
3.4 | SUECE0004 | Centre break isolator with two Earth switch (Double Break) 245kV, 2000A, 40kA for 3Sec. | Nos | 1
4 | SUE220006 | 220 kV SF6 Circuit Breaker | Nos | 0
4.1 | SUE220007 | 220 kV, 2000A, 40 kA for 3 sec, 3 pole SF6 type circuit breaker | Nos | 5
5 | SUE220008 | 220 kV Current Transformer | Nos | 0
5.1 | SUE240001 | 245kV, 40kA Current transformer (1-PH) | Nos | 15
5.2 | SUE240002 | 245kV, Current transformer (1-PH) for OPTCL | Nos | 6
5.3 | SUE240003 | 245kV Capacitive voltage transformer (1-PH) for OPTCL | Nos | 12
5.4 | SUECT0001 | CT for grid metering | Nos | 1
6 | SUE220009 | 220 kV Potential Transformer | Nos | 0
6.1 | SUE240004 | 245kV Potential transformer (1-PH) | Nos | 6
6.2 | SUEPT0001 | PT for grid metering | Nos | 1
7 | SUE220013 | 220 kV Bus Post Insulator | Nos | 1
8 | SUESU0001 | Summation metering- check metering voltage selection scheme and other associated auxiliaries related to metering | Nos | 2
9 | SUE220010 | 220 kV Erection Hardware | Nos | 0
9.1 | SUEHA0001 | Hardware Fittings | Nos | 1
9.2 | SUEDI0001 | Disc Insulator | Nos | 1
9.3 | SUECO0010 | Conductor | Nos | 1
9.4 | SUEIP0001 | IPS tube | Nos | 1
10 | SUE330003 | 33 kV Circuit Breaker | Nos | 0
10.1 | SUE330004 | 3 pole, 33 kV, 1600 A, 31.5 kA for 3 sec. SC, outdoor type Vacuum circuit breaker | Nos | 13
11 | SUE330005 | 33 kV Isolator | Nos | 0
11.1 | SUEWI0001 | With One Earth switch Centre break, 33kV, 1600A, 31.5kA 3Sec (1-PH) | Nos | 24
11.2 | SUEWI0002 | With Two Earth switch Centre break, 33kV, 1600A, 31.5kA 3Sec (1-PH) | Nos | 2
12 | SUEOU0001 | Outdoor type, 33kV class CT for 3 poles with 5 nos. cores (3 nos. PS class, 1 no. 5P20 and 1 no. Class 1.0) | Nos | 0
12.1 | SUE120001 | 1200 Amps,5 Core, 120% | Nos | 1
12.2 | SUE800001 | 800 Amps,5 Core, 150% | Nos | 1
13 | SUE330006 | 33 kV Potential Transformer | Nos | 0
13.1 | SUE330007 | 33kV/110V/√3/110V/√3 Potential transformers - 0.2S | Nos | 12
14 | SUE330008 | 33 kV Lighting Arrestor | Nos | 0
14.1 | SUECL0001 | Class III, 10 KA LA with Surge Monitor | Nos | 12
15 | SUE330009 | 33 kV Bus Post Insulator | Nos | 1
16 | SUE330010 | 33 kV Erection Hardware | Nos | 1
16.1 | SUEHA0001 | Hardware Fittings | Nos | 1
16.2 | SUEDI0001 | Disc Insulator | Nos | 1
16.3 | SUECO0010 | Conductor | Nos | 1
16.4 | SUEIP0001 | IPS tube | Nos | 1
17 | SUEFI0001 | Fibre optic Ground wire (OPGW ) | Nos | 1
18 | SUEDR0001 | Dry Type distribution Transformers-Indoor | Nos | 0
18.1 | SUE330011 | 33 kV/433 V, 630 kVA (Minimum) AN transformers along with incoming 33 kV indoor isolators | Nos | 2
18.2 | SUE330012 | 33kV isoltaor for above LT transformer | Nos | 2
19 | SUELT0001 | LT Panel | Nos | 0
19.1 | SUE410001 | 415 V Main switchboard | Nos | 1
20 | SUEMO0001 | Motor Control System (MCC). MCC shall comprise of two incomers, bus coupler and required number of outgoing feeders with 20 % spare | Nos | 1
21 | SUELT0002 | LT Squirrel Cage AC Induction Motor, 415 V, 3-ph, 50 Hz, AC | Nos | 1
22 | SUELO0001 | Local Control Station (LCS) | Nos | 1
23 | SUE220011 | 220 V, 200AH ( minimum) Plante Battery bank | Nos | 1
24 | SUE220012 | 220 V Charger twin type Float cum boost | Nos | 1
25 | SUE480001 | 48Volt 200 AH- VRLA | Nos | 1
26 | SUE480002 | 48 Volt, 40 A twin type Float cum boost | Nos | 1